## Slide 1: Grid Islanding
Grid Islanding (or simply Islanding) refers to a condition in which a distributed energy resource (DER), such as a solar photovoltaic (PV) system, wind farm, or a small power plant, continues to supply power to a portion of the grid (or a local load) even after being disconnected from the main power grid.
Types of Islanding:
  Intentional Islanding – When a microgrid or distributed generation system is deliberately separated from the main grid to ensure a reliable power supply during outages. This is common in microgrids and backup power systems.
  Unintentional Islanding – Occurs unexpectedly when the distributed generator remains connected to the local load after the main grid fails. This can pose safety risks to utility workers and damage equipment.

## Slide 2: Grid Islanding
Islanding is a critical and unsafe condition, which may occur in a power system
  This condition is caused due to an excessive use of distributed generators in the electrical grid
Islanding is the intentional isolation of a part of power system during external widespread grid disturbance
  This isolated part of Grid is called Island
  Such a disturbance may lead to black out
Therefore, islanding scheme provides a means to continue to supply power to the essential services in a zone or area
Grid is an interconnected system of Generators and Transmission Lines
  All the connected Generators run in synchronism
  However, if a major disturbance occurs, the Transmission Lines may trip which in turn may create a cascaded effect

## Slide 3: Grid Islanding
This cascaded effect, may eventually lead to collapse of entire Grid and hence black out
Islanding scheme in power system is designed in such a way that, in case of major Grid disturbance as sensed by the protection element, a portion of system is isolated by tripping the pre defined tie lines transmission lines
Thus, isolating the part of system from the remaining Grid
Thus, the effect of Grid disturbance is eliminated to affect this Island
Grid Islanding scheme is a set of protective relays, connected at the grid incomer- these relays will sense a disturbance in the grid and give a trip command to the incomer breaker whenever the grid disturbance exceeds a set limit. By opening the incomer breaker, the plant is isolated from the disturbed grid and we can keep our generator safe.

## Slide 4: Island detection system, synchronizing with the grid

## Slide 5: Island detection system, synchronizing with the grid
Islanding is defined as a condition in which a portion of utility system that contains both load and distributed generation remains energized while it is electrically isolated from the rest of the utility system
Islanding detection techniques can briefly be classified to three categories
  ML based technique
  Local detection methods, where the detection is based on the DG(Distributed Generation) side
  Remote detection methods, where the detection is based on the utility side

## Slide 6: Island detection system, synchronizing with the grid

## Slide 7: Island detection system, synchronizing with the grid
ML based technique: ML-based islanding detection techniques do not require any communication medium such as that used in remote techniques, no threshold settings as applied in passive techniques, and no power quality issues found in active techniques. The state-of-the-art techniques used for islanding detection today have shifted to ML-based islanding detection, which has certain advantages over remote and local techniques.
Remote detection methods rely on external communication devices which link each DG to the utility side. They are more reliable than the local techniques, but they are more expensive to implement.
Local detection methods can be divided into passive and active detection methods.
The performance of each type of detection scheme can be evaluated according to their non detection zone (NDZ). The NDZ represents the interval in which islanding detection scheme fails to detect islanding condition once islanding occurred

## Slide 8: Island detection system, synchronizing with the grid - Local detection methods
Passive detection methods depend on available local measurements such as frequency, voltage, phase angle, and harmonic distortion, measured on the DG site at the point of common coupling (PCC) with the grid to judge whether there is an islanding operation. These parameters vary greatly when the system is islanded.
  Voltage and current harmonics detection
  Over/under voltage and over/under frequency
  Rate of change of frequency
  Rate of change of frequency over power
  Rate of change of power output
  Voltage unbalance

## Slide 9: Island detection system, synchronizing with the grid - Local detection methods
Active detection methods
  Generally, a small fluctuation is added to the output current of the distributed power generation system. Since the utility is relatively strong in comparison with the distributed power generation system, the additional small fluctuation cannot significantly affect the local load voltage when the utility is in the nominal condition.
  Conversely, the small fluctuation can cause a significant change in frequency, amplitude or waveform of the local load voltage when the utility is interrupted. Hence, the islanding operation can be detected and judged immediately by such a change.
  Instantly, the distributed power generation system must be disconnected from the utility so as to avoid the islanding operation.
  Active frequency drift, Frequency jump, Active frequency drift with positive feedback, Variation of active and reactive power, Impedance measurement, Detection of impedance at specific frequency

## Slide 10: Island detection system, synchronizing with the grid - Local detection methods
Hybrid techniques are a combination of all the above-mentioned techniques and have a long detection time and complex implementation.
Grid synchronization attracts large concern due to the integration of renewable energy sources with the power utility grid. In order to remain interconnected while maintaining grid stability, an appropriate control technique is needed. Various RES(Renewable Energy Sources ) are synchronized by monitoring grid voltage, frequency, and phase to ensure proper operation.